## CX34 SI
ACCL Minimum Requirement Catalog Template - Standard 551/591 (SI)1,2,3,4,5
General Information
Manufacturer's Name: | Chiltrix Inc
Model Designation: | CX34
Refrigerant Designation: | R410A
Electrical Connection (V/Phase/Hz): | 230V/1/60HZ
Catalog Name and Version: | ChiltrixCX V2.3 (20230425)
Date Catalog was Created: | 2023-04-25
| 100% Load Performance Map | [11 empty] | 75% Load Performance Map |  |  | 50% Load Performance Map |  |  | 25%
Published Performance | Evaporator Leaving Water Temperature, °C | Condenser Entering Air Dry Bulb, °C | [10 empty] | Condenser Entering Air Dry Bulb, °C
|  | 12.8 | 14 | 17 | 20 | 23 | 26 | 29 | 32 | 35 | 38 | 40.6 | 25 | 27 | 29 | 17 | 19 | 21 | 13
Refrigeration Capacity, kW | 5 | 8.475 | 8.359 | 8.068 | 7.777 | 7.486 | 7.195 | 6.904 | 6.613 | 6.322 | 6.031 | 5.779 | 4.9597 | 4.7415 | 4.5232 | 3.3065 | 3.161 | 3.0155 | 1.5805
Total Power, kW |  | 1.524 | 1.57 | 1.684 | 1.798 | 1.912 | 2.026 | 2.141 | 2.255 | 2.369 | 2.483 | 2.582 | 1.0939 | 1.1478 | 1.2159 | 0.45363 | 0.47807 | 0.55637 | 0.18664
Fan Power [optional], W |  | 41 | 41 | 62 | 90 | 126 | 125 | 124 | 122 | 121 | 120 | 119 | 120 | 119 | 118 | 120 | 119 | 118 | 91
Efficiency, Cooling COP, kW/kW |  | 5.561 | 5.324 | 4.791 | 4.325 | 3.915 | 3.551 | 3.225 | 2.933 | 2.669 | 2.429 | 2.238 | 4.534 | 4.131 | 3.72 | 7.289 | 6.612 | 5.42 | 8.4683
Evaporator Water Pressure Drop, kPa |  | 15.27 | 14.92 | 14.03 | 13.14 | 12.25 | 11.37 | 10.48 | 9.59 | 8.71 | 7.82 | 7.05 | 8.71 | 8.71 | 8.71 | 8.71 | 8.71 | 8.71 | 8.71
Evaporator Entering Water Temperature, °C |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 8.9096 | 8.7376 | 8.5655 | 7.6064 | 7.4917 | 7.377 | 6.2459
Evaporator Water Flow Rate, L/s7 |  | 0.417 | 0.4 | 0.386 | 0.372 | 0.359 | 0.345 | 0.331 | 0.317 | 0.303 | 0.289 | 0.281 | 0.303 | 0.303 | 0.303 | 0.303 | 0.303 | 0.303 | 0.303
Capacity, kW | 7 | 9.04 | 8.937 | 8.678 | 8.42 | 8.162 | 8.035 | 7.908 | 7.781 | 7.654 | 6.938 | 6.317 | 5.8357 | 5.7405 | 5.2035 | 3.8905 | 3.827 | 3.469 | 1.9135
Total Power, kW |  | 1.539 | 1.574 | 1.661 | 1.748 | 1.835 | 1.967 | 2.1 | 2.232 | 2.364 | 2.5 | 2.617 | 1.1718 | 1.1502 | 1.2618 | 0.44514 | 0.47218 | 0.54553 | 0.18801
Fan Power [optional], W |  | 41 | 41 | 62 | 90 | 126 | 125 | 124 | 122 | 121 | 120 | 119 | 120 | 119 | 118 | 120 | 119 | 118 | 91
Efficiency, COP (W/W) |  | 5.874 | 5.678 | 5.225 | 4.817 | 4.448 | 4.085 | 3.766 | 3.486 | 3.238 | 2.775 | 2.414 | 4.98 | 4.991 | 4.124 | 8.74 | 8.105 | 6.359 | 10.1779
Evaporator Water Pressure Drop, kPa |  | 16.77 | 16.31 | 15.16 | 14 | 12.85 | 11.96 | 11.07 | 10.18 | 9.29 | 8.56 | 7.92 | 9.29 | 9.29 | 9.29 | 9.29 | 9.29 | 9.29 | 9.29
Evaporator Entering Water Temperature, °C |  | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 10.7774 | 10.7157 | 10.3681 | 9.5182 | 9.4771 | 9.2454 | 8.2386
Evaporator Water Flow Rate, L/s |  | 0.442 | 0.428 | 0.416 | 0.403 | 0.383 | 0.385 | 0.379 | 0.373 | 0.369 | 0.332 | 0.308 | 0.369 | 0.369 | 0.369 | 0.369 | 0.369 | 0.369 | 0.369
Capacity, kW | 9 | 9.396 | 9.32 | 9.129 | 8.938 | 8.747 | 8.57 | 8.393 | 8.215 | 8.038 | 7.477 | 6.784 | 6.1612 | 6.0285 | 5.6078 | 4.1075 | 4.019 | 3.7385 | 2.0095
Total Power, kW |  | 1.547 | 1.583 | 1.672 | 1.762 | 1.851 | 1.987 | 2.123 | 2.258 | 2.394 | 2.39 | 2.658 | 1.1361 | 1.214 | 1.2398 | 0.40281 | 0.44502 | 0.5129 | 0.16839
Fan Power [optional], W |  | 41 | 41 | 62 | 90 | 126 | 125 | 124 | 122 | 121 | 120 | 119 | 120 | 119 | 118 | 120 | 119 | 118 | 91
Efficiency, COP (W/W) |  | 6.074 | 5.888 | 5.46 | 5.073 | 4.726 | 4.313 | 3.953 | 3.638 | 3.358 | 3.128 | 2.552 | 5.423 | 4.966 | 4.523 | 10.197 | 9.031 | 7.289 | 11.9338
Evaporator Water Pressure Drop, kPa |  | 17.81 | 17.43 | 16.49 | 15.55 | 14.61 | 13.73 | 12.84 | 11.96 | 11.1 | 9.4 | 8.98 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1
Evaporator Entering Water Temperature, °C |  | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 12.8223 | 12.74 | 12.4789 | 11.5482 | 11.4933 | 11.3193 | 10.2467
Evaporator Water Flow Rate, L/s |  | 0.45 | 0.446 | 0.437 | 0.428 | 0.419 | 0.41 | 0.402 | 0.393 | 0.385 | 0.369 | 0.325 | 0.385 | 0.385 | 0.385 | 0.385 | 0.385 | 0.385 | 0.385
Capacity, kW | 11 | 9.753 | 9.706 | 9.579 | 9.453 | 9.333 | 9.106 | 8.878 | 8.651 | 8.423 | 7.796 | 7.252 | 6.4882 | 6.3172 | 5.847 | 4.3255 | 4.2115 | 3.898 | 2.1058
Total Power, kW |  | 1.555 | 1.591 | 1.68 | 1.776 | 1.866 | 2.006 | 2.145 | 2.285 | 2.424 | 2.571 | 2.698 | 1.1061 | 1.1731 | 1.187 | 0.37138 | 0.41092 | 0.47329 | 0.15411
Fan Power [optional], W |  | 41 | 41 | 62 | 90 | 126 | 125 | 124 | 122 | 121 | 120 | 119 | 120 | 119 | 118 | 120 | 119 | 118 | 91
Efficiency, COP (W/W) |  | 6.272 | 6.101 | 5.702 | 5.323 | 5.002 | 4.539 | 4.139 | 3.786 | 3.475 | 3.032 | 2.688 | 5.866 | 5.385 | 4.926 | 11.647 | 10.249 | 8.236 | 13.6636
Evaporator Water Pressure Drop, kPa |  | 18.85 | 18.56 | 17.83 | 17.1 | 16.37 | 15.49 | 14.61 | 13.72 | 12.84 | 11.34 | 10.04 | 12.84 | 12.84 | 12.84 | 12.84 | 12.84 | 12.84 | 12.84
Evaporator Entering Water Temperature, °C |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 14.8454 | 14.744 | 14.4653 | 13.5636 | 13.496 | 13.3102 | 12.248
Evaporator Water Flow Rate, L/s |  | 0.467 | 0.465 | 0.459 | 0.453 | 0.447 | 0.436 | 0.425 | 0.414 | 0.403 | 0.373 | 0.347 | 0.403 | 0.403 | 0.403 | 0.403 | 0.403 | 0.403 | 0.403
Capacity, kW | 13 | 10.109 | 10.09 | 10.03 | 9.97 | 9.918 | 9.64 | 9.363 | 9.085 | 8.807 | 8.224 | 7.719 | 6.8137 | 6.6052 | 6.168 | 4.5425 | 4.4035 | 4.112 | 2.2018
Total Power, kW |  | 1.563 | 1.6 | 1.69 | 1.79 | 1.882 | 2.025 | 2.169 | 2.312 | 2.455 | 2.607 | 2.739 | 1.08 | 1.138 | 1.158 | 0.34675 | 0.40134 | 0.4484 | 0.16126
Fan Power [optional], W |  | 41 | 41 | 62 | 90 | 126 | 125 | 124 | 122 | 121 | 120 | 119 | 120 | 119 | 118 | 120 | 119 | 118 | 91
Efficiency, COP (W/W) |  | 6.4677 | 6.3062 | 5.9349 | 5.5698 | 5.2699 | 4.7605 | 4.3167 | 3.9295 | 3.5874 | 3.1546 | 2.8182 | 6.3093 | 5.804 | 5.3264 | 13.1003 | 10.972 | 9.1703 | 13.6533
Evaporator Water Pressure Drop, kPa |  | 19.89 | 19.68 | 19.17 | 18.65 | 18.13 | 17.25 | 16.38 | 15.5 | 14.62 | 12.73 | 11.1 | 14.62 | 14.62 | 14.62 | 14.62 | 14.62 | 14.62 | 14.62
Evaporator Entering Water Temperature, °C |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 16.8565 | 16.7385 | 16.491 | 15.571 | 15.4923 | 15.3273 | 14.2462
Evaporator Water Flow Rate, L/s |  | 0.486 | 0.483 | 0.48 | 0.477 | 0.467 | 0.462 | 0.448 | 0.435 | 0.422 | 0.394 | 0.369 | 0.422 | 0.422 | 0.422 | 0.422 | 0.422 | 0.422 | 0.422
Capacity, kW | 15 | 10.48 | 10.45 | 10.36 | 10.28 | 10.2 | 9.948 | 9.696 | 9.444 | 9.192 | 8.716 | 8.304 | 7.083 | 6.894 | 6.537 | 4.722 | 4.596 | 4.358 | 2.298
Total Power, kW |  | 1.59 | 1.62 | 1.69 | 1.77 | 1.84 | 2.001 | 2.163 | 2.324 | 2.485 | 2.636 | 2.767 | 1.049 | 1.108 | 1.141 | 0.32487 | 0.36318 | 0.43144 | 0.13461
Fan Power [optional], W |  | 41 | 41 | 62 | 90 | 126 | 125 | 124 | 122 | 121 | 120 | 119 | 120 | 119 | 118 | 120 | 119 | 118 | 91
Efficiency, COP (W/W) |  | 6.591 | 6.451 | 6.13 | 5.808 | 5.543 | 4.972 | 4.483 | 4.064 | 3.699 | 3.307 | 3.001 | 6.752 | 6.222 | 5.729 | 14.535 | 12.655 | 10.101 | 17.0715
Evaporator Water Pressure Drop, kPa |  | 20.65 | 20.52 | 20.21 | 19.89 | 19.58 | 18.79 | 17.99 | 17.2 | 16.4 | 14.71 | 13.25 | 16.4 | 16.4 | 16.4 | 16.4 | 16.4 | 16.4 | 16.4
Evaporator Entering Water Temperature, °C |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 18.8449 | 18.7423 | 18.5485 | 17.5633 | 17.4949 | 17.3657 | 16.2474
Evaporator Water Flow Rate, L/s |  | 0.502 | 0.5 | 0.496 | 0.492 | 0.489 | 0.476 | 0.464 | 0.452 | 0.44 | 0.417 | 0.398 | 0.44 | 0.44 | 0.44 | 0.44 | 0.44 | 0.44 | 0.44
Capacity, kW | 15.6 | 10.586 | 10.55 | 10.46 | 10.38 | 10.288 | 10.043 | 9.798 | 9.552 | 9.307 | 8.863 | 8.479 | 7.164 | 6.9802 | 6.6472 | 4.776 | 4.6535 | 4.4315 | 2.3268
Total Power, kW |  | 1.592 | 1.62 | 1.69 | 1.76 | 1.829 | 1.995 | 2.162 | 2.328 | 2.494 | 2.645 | 2.776 | 1.0401 | 1.1001 | 1.1361 | 0.3188 | 0.35697 | 0.42643 | 0.13251
Fan Power [optional], W |  | 41 | 41 | 62 | 90 | 126 | 125 | 124 | 122 | 121 | 120 | 119 | 120 | 119 | 118 | 120 | 119 | 118 | 91
Efficiency, COP (W/W) |  | 6.649 | 6.512 | 6.189 | 5.898 | 5.625 | 5.034 | 4.532 | 4.103 | 3.732 | 3.351 | 3.054 | 6.888 | 6.345 | 5.851 | 14.981 | 13.036 | 10.392 | 17.5585
Evaporator Water Pressure Drop, kPa |  | 20.88 | 20.78 | 20.53 | 20.27 | 20.02 | 19.25 | 18.48 | 17.7 | 16.93 | 15.3 | 13.89 | 16.93 | 16.93 | 16.93 | 16.93 | 16.93 | 16.93 | 16.93
Evaporator Entering Water Temperature, °C |  | 20.6 | 20.6 | 20.6 | 20.6 | 20.6 | 20.6 | 20.6 | 20.6 | 20.6 | 20.6 | 20.6 | 19.336 | 19.2402 | 19.0665 | 18.0907 | 18.0268 | 17.911 | 16.8134
Evaporator Water Flow Rate, L/s |  | 0.503 | 0.505 | 0.501 | 0.497 | 0.492 | 0.481 | 0.469 | 0.457 | 0.458 | 0.424 | 0.414 | 0.458 | 0.458 | 0.458 | 0.458 | 0.458 | 0.458 | 0.458
IPLV Calculation
Published Performance | Evaporator Leaving Water Temperature, °C | Condenser Entering Air Dry Bulb, °C and % Load
|  | 35, 100% |  | 27, 75% |  | 19, 50% |  | 13, 25%
Capacity, kW | 7 | 7.654 |  | 5.7405 |  | 3.827 |  | 1.9135
Total Power, kW |  | 2.364 |  | 1.1501 |  | 0.4722 |  | 0.18801
Efficiency, COP (W/W) |  | 3.238 |  | 4.9913 |  | 8.1045 |  | 10.1775
| IPLV.SI | 6.9971 | kW/kW
Published Performance | Evaporator Leaving Water Temperature, °C | Condenser Entering Air Dry Bulb, °C and % Load
|  | 35, 100% |  | 27, 75% |  | 19, 50% |  | 13, 25%
Capacity, kW | 13 | 8.807 |  | 6.6052 |  | 4.4035 |  | 2.2018
Total Power, kW |  | 2.455 |  | 1.1381 |  | 0.40134 |  | 0.16126
Efficiency, COP (W/W) |  | 3.587 |  | 5.804 |  | 10.972 |  | 13.6535
| NPLV.SI | 9.0494 | kW/kW
Proper claims to AHRI Certification
Certified in accordance with the AHRI Air-Cooled Water-Chilling Packages Certification Program, which is based on AHRI Standard 550/590 (I-P) and AHRI Standard 551/591 (SI). Certified units may be found in the AHRI Directory at www.ahridirectory.org
AHRI Mark
Notes
1. The following apply to all ratings shown above: Evaporator Fouling Factor: 0.0180 m2·K/kW Condenser Fouling Factor: 0.000 m2·K/kW Atmospheric Pressure: 101.33 kPa 2. Highlighted fields represent the minimum required inputs. For units with continuous unloading, highlighted fields shall be provided. For units with discrete capacity steps, performance at each capacity step shall be provided. 3. All interpolated data within a units published performance is suject to AHRI testing. 4. All Published ratings for this unit shall be included in the values shown above. Performance at different conditions (i.e. different air and water temperatures, water flow rates, atmospheric pressures, fouling factors, etc.) shall not be published. 5. All values shall have the correct significant figures as in Table 8 of AHRI 551/591. 6. Full-Load Evaporator Water Temperature Change: 5.00°C. 7. Evaporator flow rates are to be held constant at full-load values for all part-load conditions.

## CX50 SI
ACCL Minimum Requirement Catalog Template - Standard 551/591 (SI)1,2,3,4,5
General Information
Manufacturer's Name: | Chiltrix Inc
Model Number: | CX50
Refrigerant Designation: | R32
Electrical Connection (V/Phase/Hz): | 230V/1/60HZ
Catalog Name and Version: | ChiltrixCX V2.3 (20230425)
Date Catalog was Created: | 2023-04-25
Published Performance | Evaporator Leaving Water Temperature, °C6 | 100% Load Performance Map | [10 empty] | 75% Load Performance Map |  |  | 50% Load Performance Map |  |  | 25%
|  | Condenser Entering Air Dry Bulb, °C | [10 empty] | Condenser Entering Air Dry Bulb, °C
|  | 12.8 | 14 | 17 | 20 | 23 | 26 | 29 | 32 | 35 | 38 | 40.6 | 25 | 27 | 29 | 17 | 19 | 21 | 13
Refrigeration Capacity, kW | 5 | 14.927 | 14.731 | 14.241 | 13.751 | 13.261 | 12.77 | 12.28 | 11.79 | 11.3 | 10.81 | 10.385 | 8.8425 | 8.475 | 8.1075 | 5.895 | 5.65 | 5.405 | 2.825
Total Power, kW |  | 2.508 | 2.593 | 2.804 | 3.015 | 3.227 | 3.438 | 3.65 | 3.861 | 4.072 | 4.284 | 4.467 | 2.118 | 2.2093 | 2.2653 | 0.89822 | 0.95278 | 1.0471 | 0.35538
Fan Power [optional], W |  | 82 | 82 | 124 | 180 | 252 | 250 | 247 | 245 | 242 | 240 | 238 | 240 | 237 | 235 | 240 | 237 | 235 | 182
Efficiency, Cooling COP, kW/kW |  | 5.952 | 5.681 | 5.079 | 4.561 | 4.109 | 3.714 | 3.364 | 3.054 | 2.775 | 2.523 | 2.325 | 4.175 | 3.836 | 3.579 | 6.563 | 5.93 | 5.162 | 7.9492
Evaporator Water Pressure Drop, kPa |  | 31.54 | 31.54 | 31.54 | 31.54 | 31.54 | 31.54 | 31.54 | 31.54 | 31.54 | 31.54 | 31.54 | 31.54 | 31.54 | 31.54 | 31.54 | 31.54 | 31.54 | 31.54
Evaporator Entering Water Temperature, °C |  | 11.5901 | 11.5036 | 11.2873 | 11.0709 | 10.8546 | 10.6378 | 10.4215 | 10.2052 | 9.9888 | 9.7725 | 9.5849 | 8.9039 | 8.7416 | 8.5794 | 7.6026 | 7.4944 | 7.3863 | 6.2472
Evaporator Water Flow Rate, L/s |  | 0.541 | 0.541 | 0.541 | 0.541 | 0.541 | 0.541 | 0.541 | 0.541 | 0.541 | 0.541 | 0.541 | 0.541 | 0.541 | 0.541 | 0.541 | 0.541 | 0.541 | 0.541
Refrigeration Capacity, kW | 7 | 15.819 | 15.618 | 15.115 | 14.613 | 14.11 | 13.608 | 13.105 | 12.603 | 12.1 | 11.484 | 10.95 | 9.4522 | 9.075 | 8.613 | 6.3015 | 6.05 | 5.742 | 3.025
Total Power, kW |  | 2.499 | 2.581 | 2.787 | 2.992 | 3.198 | 3.403 | 3.609 | 3.814 | 4.02 | 4.263 | 4.473 | 2.0154 | 2.0602 | 2.1532 | 0.82394 | 0.86602 | 0.94643 | 0.3066
Fan Power [optional], W |  | 82 | 82 | 124 | 180 | 252 | 250 | 247 | 245 | 242 | 240 | 238 | 240 | 237 | 235 | 240 | 237 | 235 | 182
Efficiency, Cooling COP, kW/kW |  | 6.33 | 6.051 | 5.423 | 4.884 | 4.412 | 3.999 | 3.631 | 3.304 | 3.01 | 2.694 | 2.448 | 4.69 | 4.405 | 4 | 7.648 | 6.986 | 6.067 | 9.8661
Evaporator Water Pressure Drop, kPa |  | 31.8 | 31.8 | 31.8 | 31.8 | 31.8 | 31.8 | 31.8 | 31.8 | 31.8 | 31.8 | 31.8 | 31.8 | 31.8 | 31.8 | 31.8 | 31.8 | 31.8 | 31.8
Evaporator Entering Water Temperature, °C |  | 13.5143 | 13.4315 | 13.2244 | 13.0177 | 12.8105 | 12.6038 | 12.3967 | 12.19 | 11.9828 | 11.7291 | 11.5092 | 10.8925 | 10.7371 | 10.5469 | 9.595 | 9.4914 | 9.3646 | 8.2457
Evaporator Water Flow Rate, L/s |  | 0.58 | 0.58 | 0.58 | 0.58 | 0.58 | 0.58 | 0.58 | 0.58 | 0.58 | 0.58 | 0.58 | 0.58 | 0.58 | 0.58 | 0.58 | 0.58 | 0.58 | 0.58
Refrigeration Capacity, kW | 9 | 16.326 | 16.154 | 15.725 | 15.296 | 14.867 | 14.361 | 13.856 | 13.35 | 12.844 | 12.218 | 11.676 | 10.0125 | 9.633 | 9.1635 | 6.675 | 6.422 | 6.109 | 3.211
Total Power, kW |  | 2.544 | 2.618 | 2.804 | 2.99 | 3.176 | 3.395 | 3.613 | 3.832 | 4.05 | 4.303 | 4.523 | 1.924 | 2.006 | 2.0737 | 0.76452 | 0.80608 | 0.87622 | 0.27665
Fan Power [optional], W |  | 82 | 82 | 124 | 180 | 252 | 250 | 247 | 245 | 242 | 240 | 238 | 240 | 237 | 235 | 240 | 237 | 235 | 182
Efficiency, Cooling COP, kW/kW |  | 6.417 | 6.17 | 5.608 | 5.116 | 4.681 | 4.23 | 3.835 | 3.484 | 3.171 | 2.839 | 2.581 | 5.204 | 4.802 | 4.419 | 8.731 | 7.967 | 6.972 | 11.6069
Evaporator Water Pressure Drop, kPa |  | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1
Evaporator Entering Water Temperature, °C |  | 15.3405 | 15.2737 | 15.1071 | 14.9405 | 14.7739 | 14.5773 | 14.3812 | 14.1847 | 13.9882 | 13.7451 | 13.5346 | 12.8885 | 12.7411 | 12.5588 | 11.5924 | 11.4941 | 11.3725 | 10.247
Evaporator Water Flow Rate, L/s |  | 0.615 | 0.615 | 0.615 | 0.615 | 0.615 | 0.615 | 0.615 | 0.615 | 0.615 | 0.615 | 0.615 | 0.615 | 0.615 | 0.615 | 0.615 | 0.615 | 0.615 | 0.615
Refrigeration Capacity, kW | 11 | 16.834 | 16.693 | 16.338 | 15.978 | 15.623 | 15.114 | 14.606 | 14.097 | 13.588 | 12.953 | 12.402 | 10.5727 | 10.191 | 9.7148 | 7.0485 | 6.794 | 6.4765 | 3.397
Total Power, kW |  | 2.589 | 2.654 | 2.822 | 2.984 | 3.153 | 3.385 | 3.617 | 3.848 | 4.08 | 4.344 | 4.572 | 1.85 | 1.9294 | 2.0084 | 0.71836 | 0.75657 | 0.82252 | 0.2529
Fan Power [optional], W |  | 82 | 82 | 124 | 180 | 252 | 250 | 247 | 245 | 242 | 240 | 238 | 240 | 237 | 235 | 240 | 237 | 235 | 182
Efficiency, Cooling COP, kW/kW |  | 6.502 | 6.29 | 5.79 | 5.355 | 4.955 | 4.465 | 4.038 | 3.663 | 3.33 | 2.982 | 2.713 | 5.715 | 5.282 | 4.837 | 9.812 | 8.98 | 7.874 | 13.4322
Evaporator Water Pressure Drop, kPa |  | 40.4 | 40.4 | 40.4 | 40.4 | 40.4 | 40.4 | 40.4 | 40.4 | 40.4 | 40.4 | 40.4 | 40.4 | 40.4 | 40.4 | 40.4 | 40.4 | 40.4 | 40.4
Evaporator Entering Water Temperature, °C |  | 17.1762 | 17.1245 | 16.9943 | 16.8622 | 16.7319 | 16.5452 | 16.3588 | 16.1721 | 15.9853 | 15.7523 | 15.5502 | 14.879 | 14.739 | 14.5643 | 13.586 | 13.4927 | 13.3762 | 12.2463
Evaporator Water Flow Rate, L/s |  | 0.651 | 0.651 | 0.651 | 0.651 | 0.651 | 0.651 | 0.651 | 0.651 | 0.651 | 0.651 | 0.651 | 0.651 | 0.651 | 0.651 | 0.651 | 0.651 | 0.651 | 0.651
Refrigeration Capacity, kW | 13 | 17.341 | 17.23 | 16.95 | 16.66 | 16.38 | 15.868 | 15.357 | 14.845 | 14.333 | 13.687 | 13.128 | 11.1337 | 10.7498 | 10.2652 | 7.4225 | 7.1665 | 6.8435 | 3.5833
Total Power, kW |  | 2.634 | 2.69 | 2.84 | 2.98 | 3.131 | 3.376 | 3.621 | 3.866 | 4.111 | 4.385 | 4.622 | 1.7863 | 1.8634 | 1.9519 | 0.68103 | 0.70913 | 0.77873 | 0.23471
Fan Power [optional], W |  | 82 | 82 | 124 | 180 | 252 | 250 | 247 | 245 | 242 | 240 | 238 | 240 | 237 | 235 | 240 | 237 | 235 | 182
Efficiency, Cooling COP, kW/kW |  | 6.584 | 6.405 | 5.968 | 5.591 | 5.232 | 4.7 | 4.241 | 3.84 | 3.486 | 3.121 | 2.84 | 6.233 | 5.769 | 5.259 | 10.899 | 10.106 | 8.788 | 15.2664
Evaporator Water Pressure Drop, kPa |  | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6
Evaporator Entering Water Temperature, °C |  | 19.0376 | 18.999 | 18.9015 | 18.8005 | 18.7031 | 18.5248 | 18.3469 | 18.1686 | 17.9903 | 17.7654 | 17.5708 | 16.8765 | 16.7428 | 16.5741 | 15.5843 | 15.4952 | 15.3827 | 14.2476
Evaporator Water Flow Rate, L/s |  | 0.686 | 0.686 | 0.686 | 0.686 | 0.686 | 0.686 | 0.686 | 0.686 | 0.686 | 0.686 | 0.686 | 0.686 | 0.686 | 0.686 | 0.686 | 0.686 | 0.686 | 0.686
Refrigeration Capacity, kW | 15 | 18.14 | 17.99 | 17.6 | 17.22 | 16.83 | 16.392 | 15.954 | 15.515 | 15.077 | 14.371 | 13.76 | 11.6363 | 11.3078 | 10.7782 | 7.7575 | 7.5385 | 7.1855 | 3.7692
Total Power, kW |  | 2.56 | 2.63 | 2.8 | 2.97 | 3.14 | 3.39 | 3.641 | 3.891 | 4.141 | 4.402 | 4.628 | 1.7252 | 1.8104 | 1.8979 | 0.64711 | 0.68432 | 0.74146 | 0.22063
Fan Power [optional], W |  | 82 | 82 | 124 | 180 | 252 | 250 | 247 | 245 | 242 | 240 | 238 | 240 | 237 | 235 | 240 | 237 | 235 | 182
Efficiency, Cooling COP, kW/kW |  | 7.086 | 6.84 | 6.286 | 5.798 | 5.36 | 4.835 | 4.382 | 3.987 | 3.641 | 3.265 | 2.973 | 6.745 | 6.246 | 5.679 | 11.988 | 11.016 | 9.691 | 17.0839
Evaporator Water Pressure Drop, kPa |  | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9
Evaporator Entering Water Temperature, °C |  | 21.0009 | 20.9513 | 20.8223 | 20.6966 | 20.5676 | 20.4227 | 20.2778 | 20.1325 | 19.9876 | 19.7541 | 19.552 | 18.8494 | 18.7407 | 18.5656 | 17.5663 | 17.4938 | 17.377 | 16.2469
Evaporator Water Flow Rate, L/s |  | 0.722 | 0.722 | 0.722 | 0.722 | 0.722 | 0.722 | 0.722 | 0.722 | 0.722 | 0.722 | 0.722 | 0.722 | 0.722 | 0.722 | 0.722 | 0.722 | 0.722 | 0.722
Refrigeration Capacity, kW | 15.6 | 18.38 | 18.21 | 17.8 | 17.38 | 16.965 | 16.549 | 16.133 | 15.716 | 15.3 | 14.577 | 13.95 | 11.787 | 11.475 | 10.9328 | 7.858 | 7.65 | 7.2885 | 3.825
Total Power, kW |  | 2.535 | 2.61 | 2.78 | 2.96 | 3.138 | 3.391 | 3.644 | 3.897 | 4.15 | 4.407 | 4.63 | 1.7085 | 1.7952 | 1.8837 | 0.6385 | 0.67532 | 0.7317 | 0.21708
Fan Power [optional], W |  | 82 | 82 | 124 | 180 | 252 | 250 | 247 | 245 | 242 | 240 | 238 | 240 | 237 | 235 | 240 | 237 | 235 | 182
Efficiency, Cooling COP, kW/kW |  | 7.25 | 6.977 | 6.403 | 5.872 | 5.406 | 4.88 | 4.427 | 4.033 | 3.687 | 3.308 | 3.013 | 6.899 | 6.392 | 5.804 | 12.307 | 11.328 | 9.961 | 17.6199
Evaporator Water Pressure Drop, kPa |  | 50.2 | 50.2 | 50.2 | 50.2 | 50.2 | 50.2 | 50.2 | 50.2 | 50.2 | 50.2 | 50.2 | 50.2 | 50.2 | 50.2 | 50.2 | 50.2 | 50.2 | 50.2
Evaporator Entering Water Temperature, °C |  | 21.5891 | 21.5337 | 21.4001 | 21.2632 | 21.128 | 20.9924 | 20.8569 | 20.721 | 20.5855 | 20.3499 | 20.1456 | 19.4408 | 19.3391 | 19.1624 | 18.1605 | 18.0927 | 17.9749 | 16.8464
Evaporator Water Flow Rate, L/s |  | 0.733 | 0.733 | 0.733 | 0.733 | 0.733 | 0.733 | 0.733 | 0.733 | 0.733 | 0.733 | 0.733 | 0.733 | 0.733 | 0.733 | 0.733 | 0.733 | 0.733 | 0.733
IPLV.SI Calculation
Published Performance | Evaporator Leaving Water Temperature, °C7 | Condenser Entering Air Dry Bulb, °C and % Load
|  | 35.0, 100% |  | 27.0, 75% |  | 19.0, 50% |  | 13.0, 25%
Refrigeration Capacity, kW | 7 | 12.1 |  | 9.075 |  | 6.05 |  | 3.025
Total Power, kW |  | 4.02 |  | 2.0601 |  | 0.86603 |  | 0.30659
Efficiency, Cooling COP (kW/kW) |  | 3.01 |  | 4.4051 |  | 6.9859 |  | 9.8665
| IPLV.SI | 6.2078 | kW/kW
Published Performance | Evaporator Leaving Water Temperature, °C | Condenser Entering Air Dry Bulb, °C and % Load
|  | 35, 100% |  | 27, 75% |  | 19, 50% |  | 13, 25%
Capacity, kW | 13 | 14.33 |  | 10.7475 |  | 7.165 |  | 3.5825
Total Power, kW |  | 4.111 |  | 1.863 |  | 0.70898 |  | 0.23467
Efficiency, COP (W/W) |  | 3.486 |  | 5.769 |  | 10.106 |  | 15.2662
| NPLV.SI | 8.8375 | kW/kW
Proper claims to AHRI Certification
Certified in accordance with the AHRI Air-Cooled Water-Chilling Packages Certification Program, which is based on AHRI Standard 550/590 (I-P) and AHRI Standard 551/591 (SI). Certified units may be found in the AHRI Directory at www.ahridirectory.org
AHRI Mark
Notes
1. The following apply to all ratings shown above: Evaporator Fouling Factor: 0.0180 m2·K/kW Condenser Fouling Factor: 0.000 m2·K/kW Atmospheric Pressure: 101.33 kPa 2. Highlighted fields represent the minimum required inputs. For units with continuous unloading, highlighted fields shall be provided. For units with discrete capacity steps, performance at each capacity step shall be provided. 3. All interpolated data within a units published performance is suject to AHRI testing. 4. All Published ratings for this unit shall be included in the values shown above. Performance at different conditions (i.e. different air and water temperatures, water flow rates, atmospheric pressures, fouling factors, etc.) shall not be published. 5. All values shall have the correct significant figures as in Table 8 of AHRI 551/591. 6. Full-Load Evaporator Water Temperature Change: 5.00°C. 7. Evaporator flow rates are to be held constant at full-load values for all part-load conditions.

## CX35 SI
ACCL Minimum Requirement Catalog Template - Standard 551/591 (SI)1,2,3,4,5
General Information
Manufacturer's Name: | Chiltrix Inc
Model Number: | CX35
Refrigerant Designation: | R32
Electrical Connection (V/Phase/Hz): | 230V/1/60HZ
Catalog Name and Version: | ChiltrixCX V2.3 (20230425)
Date Catalog was Created: | 2023-04-25
Published Performance | Evaporator Leaving Water Temperature, °C6 | 100% Load Performance Map | [10 empty] | 75% Load Performance Map |  |  | 50% Load Performance Map |  |  | 25%
|  | Condenser Entering Air Dry Bulb, °C | [10 empty] | Condenser Entering Air Dry Bulb, °C
|  | 12.8 | 14 | 17 | 20 | 23 | 26 | 29 | 32 | 35 | 38 | 40.6 | 25 | 27 | 29 | 17 | 19 | 21 | 13
Refrigeration Capacity, kW | 5 | 9.146 | 9.007 | 8.66 | 8.313 | 7.966 | 7.619 | 7.271 | 6.924 | 6.625 | 6.23 | 5.929 | 5.193 | 4.9688 | 4.6725 | 3.462 | 3.3125 | 3.115 | 1.6562
Total Power, kW |  | 1.468 | 1.523 | 1.659 | 1.795 | 1.932 | 2.068 | 2.205 | 2.341 | 2.431 | 2.614 | 2.732 | 1.2604 | 1.2611 | 1.2794 | 0.43839 | 0.48133 | 0.49968 | 0.17345
Fan Power [optional], W |  | 51 | 57 | 88 | 97 | 114 | 117 | 120 | 121 | 125 | 125.3 | 127 | 117 | 119 | 120 | 73 | 79 | 84 | 43
Efficiency, Cooling COP, kW/kW |  | 6.23 | 5.914 | 5.22 | 4.631 | 4.123 | 3.684 | 3.298 | 2.958 | 2.725 | 2.383 | 2.17 | 4.12 | 3.94 | 3.652 | 7.897 | 6.882 | 6.234 | 9.549
Evaporator Water Pressure Drop, kPa |  | 16.231 | 16.231 | 16.231 | 16.231 | 16.231 | 16.231 | 16.231 | 16.231 | 16.231 | 16.231 | 16.231 | 16.231 | 16.231 | 16.231 | 16.231 | 16.231 | 16.231 | 16.231
Evaporator Entering Water Temperature, °C |  | 11.8265 | 11.7228 | 11.4638 | 11.2048 | 10.9458 | 10.6868 | 10.427 | 10.168 | 9.9449 | 9.65 | 9.4254 | 8.876 | 8.7086 | 8.4875 | 7.584 | 7.4724 | 7.325 | 6.2362
Evaporator Water Flow Rate, L/s |  | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32
Refrigeration Capacity, kW | 7 | 9.807 | 9.665 | 9.31 | 8.956 | 8.601 | 8.212 | 7.823 | 7.434 | 7.045 | 6.759 | 6.511 | 5.5755 | 5.2838 | 5.0693 | 3.717 | 3.5225 | 3.3795 | 1.7612
Total Power, kW |  | 1.459 | 1.513 | 1.646 | 1.78 | 1.914 | 2.022 | 2.13 | 2.237 | 2.345 | 2.572 | 2.769 | 1.2134 | 1.171 | 1.2645 | 0.42176 | 0.46367 | 0.48127 | 0.17331
Fan Power [optional], W |  | 51 | 57 | 88 | 97 | 114 | 117 | 120 | 121 | 125 | 125.3 | 127 | 117 | 119 | 120 | 73 | 79 | 84 | 43
Efficiency, Cooling COP, kW/kW |  | 6.722 | 6.388 | 5.656 | 5.031 | 4.494 | 4.061 | 3.673 | 3.323 | 3.004 | 2.628 | 2.351 | 4.595 | 4.512 | 4.009 | 8.813 | 7.597 | 7.022 | 10.1624
Evaporator Water Pressure Drop, kPa |  | 16.651 | 16.651 | 16.651 | 16.651 | 16.651 | 16.651 | 16.651 | 16.651 | 16.651 | 16.651 | 16.651 | 16.651 | 16.651 | 16.651 | 16.651 | 16.651 | 16.651 | 16.651
Evaporator Entering Water Temperature, °C |  | 14.0861 | 13.9835 | 13.727 | 13.4712 | 13.2147 | 12.9337 | 12.6526 | 12.3715 | 12.0904 | 11.8838 | 11.7046 | 11.0286 | 10.8178 | 10.6628 | 9.6858 | 9.5452 | 9.4419 | 8.2726
Evaporator Water Flow Rate, L/s |  | 0.33056 | 0.33056 | 0.33056 | 0.33056 | 0.33056 | 0.33056 | 0.33056 | 0.33056 | 0.33056 | 0.33056 | 0.33056 | 0.33056 | 0.33056 | 0.33056 | 0.33056 | 0.33056 | 0.33056 | 0.33056
Refrigeration Capacity, kW | 9 | 10.559 | 10.409 | 10.036 | 9.662 | 9.288 | 8.898 | 8.508 | 8.118 | 7.728 | 7.425 | 7.113 | 6.0885 | 5.796 | 5.5687 | 4.059 | 3.864 | 3.7125 | 1.932
Total Power, kW |  | 1.454 | 1.51 | 1.649 | 1.789 | 1.928 | 2.051 | 2.173 | 2.296 | 2.418 | 2.682 | 2.823 | 1.1962 | 1.2182 | 1.2764 | 0.41609 | 0.4416 | 0.47179 | 0.16352
Fan Power [optional], W |  | 51 | 57 | 88 | 97 | 114 | 117 | 120 | 121 | 125 | 125.3 | 127 | 117 | 119 | 120 | 73 | 79 | 84 | 43
Efficiency, Cooling COP, kW/kW |  | 7.262 | 6.893 | 6.086 | 5.401 | 4.817 | 4.338 | 3.915 | 3.536 | 3.196 | 2.768 | 2.52 | 5.09 | 4.758 | 4.363 | 9.755 | 8.75 | 7.869 | 11.8151
Evaporator Water Pressure Drop, kPa |  | 19.74 | 19.74 | 19.74 | 19.74 | 19.74 | 19.74 | 19.74 | 19.74 | 19.74 | 19.74 | 19.74 | 19.74 | 19.74 | 19.74 | 19.74 | 19.74 | 19.74 | 19.74
Evaporator Entering Water Temperature, °C |  | 15.8161 | 15.7193 | 15.4785 | 15.2371 | 14.9957 | 14.7439 | 14.4922 | 14.2404 | 13.9887 | 13.7931 | 13.5917 | 12.9303 | 12.7415 | 12.5948 | 11.6202 | 11.4943 | 11.3965 | 10.2472
Evaporator Water Flow Rate, L/s |  | 0.37 | 0.37 | 0.37 | 0.37 | 0.37 | 0.37 | 0.37 | 0.37 | 0.37 | 0.37 | 0.37 | 0.37 | 0.37 | 0.37 | 0.37 | 0.37 | 0.37 | 0.37
Refrigeration Capacity, kW | 11 | 11.311 | 11.155 | 10.763 | 10.365 | 9.976 | 9.585 | 9.193 | 8.802 | 8.41 | 8.038 | 7.715 | 6.6015 | 6.3075 | 6.0285 | 4.401 | 4.205 | 4.019 | 2.1025
Total Power, kW |  | 1.449 | 1.504 | 1.649 | 1.8 | 1.942 | 2.08 | 2.217 | 2.355 | 2.492 | 2.699 | 2.878 | 1.1774 | 1.2193 | 1.2775 | 0.41108 | 0.4304 | 0.45952 | 0.15352
Fan Power [optional], W |  | 51 | 57 | 88 | 97 | 114 | 117 | 120 | 121 | 125 | 125.3 | 127 | 117 | 119 | 120 | 73 | 79 | 84 | 43
Efficiency, Cooling COP, kW/kW |  | 7.806 | 7.417 | 6.527 | 5.758 | 5.137 | 4.608 | 4.147 | 3.738 | 3.375 | 2.978 | 2.681 | 5.607 | 5.173 | 4.719 | 10.706 | 9.77 | 8.746 | 13.6955
Evaporator Water Pressure Drop, kPa |  | 22.83 | 22.83 | 22.83 | 22.83 | 22.83 | 22.83 | 22.83 | 22.83 | 22.83 | 22.83 | 22.83 | 22.83 | 22.83 | 22.83 | 22.83 | 22.83 | 22.83 | 22.83
Evaporator Entering Water Temperature, °C |  | 17.7037 | 17.6112 | 17.3789 | 17.143 | 16.9125 | 16.6807 | 16.4484 | 16.2167 | 15.9844 | 15.7639 | 15.5724 | 14.9125 | 14.7383 | 14.5729 | 13.6083 | 13.4922 | 13.3819 | 12.2461
Evaporator Water Flow Rate, L/s |  | 0.403 | 0.403 | 0.403 | 0.403 | 0.403 | 0.403 | 0.403 | 0.403 | 0.403 | 0.403 | 0.403 | 0.403 | 0.403 | 0.403 | 0.403 | 0.403 | 0.403 | 0.403
Refrigeration Capacity, kW | 13 | 12.063 | 11.9 | 11.49 | 11.07 | 10.663 | 10.271 | 9.878 | 9.486 | 9.014 | 8.677 | 8.317 | 7.1145 | 6.7605 | 6.5077 | 4.743 | 4.507 | 4.3385 | 2.2535
Total Power, kW |  | 1.444 | 1.5 | 1.65 | 1.81 | 1.956 | 2.108 | 2.261 | 2.413 | 2.619 | 2.762 | 2.932 | 1.1576 | 1.185 | 1.2838 | 0.405 | 0.41631 | 0.44741 | 0.13829
Fan Power [optional], W |  | 51 | 57 | 88 | 97 | 114 | 117 | 120 | 121 | 125 | 125.3 | 127 | 117 | 119 | 120 | 73 | 79 | 84 | 43
Efficiency, Cooling COP, kW/kW |  | 8.354 | 7.933 | 6.964 | 6.116 | 5.451 | 4.872 | 4.369 | 3.931 | 3.442 | 3.142 | 2.837 | 6.146 | 5.705 | 5.069 | 11.711 | 10.826 | 9.697 | 16.296
Evaporator Water Pressure Drop, kPa |  | 25.91 | 25.91 | 25.91 | 25.91 | 25.91 | 25.91 | 25.91 | 25.91 | 25.91 | 25.91 | 25.91 | 25.91 | 25.91 | 25.91 | 25.91 | 25.91 | 25.91 | 25.91
Evaporator Entering Water Temperature, °C |  | 19.6234 | 19.5339 | 19.3088 | 19.0782 | 18.8547 | 18.6395 | 18.4237 | 18.2085 | 17.9493 | 17.7643 | 17.5666 | 16.9064 | 16.712 | 16.5732 | 15.6042 | 15.4747 | 15.3821 | 14.2373
Evaporator Water Flow Rate, L/s |  | 0.435 | 0.435 | 0.435 | 0.435 | 0.435 | 0.435 | 0.435 | 0.435 | 0.435 | 0.435 | 0.435 | 0.435 | 0.435 | 0.435 | 0.435 | 0.435 | 0.435 | 0.435
Refrigeration Capacity, kW | 15 | 12.84 | 12.68 | 12.26 | 11.85 | 11.44 | 11.024 | 10.608 | 10.191 | 9.775 | 9.332 | 8.948 | 7.6433 | 7.3312 | 6.999 | 5.0955 | 4.8875 | 4.666 | 2.4438
Total Power, kW |  | 1.43 | 1.49 | 1.65 | 1.81 | 1.97 | 2.137 | 2.304 | 2.471 | 2.638 | 2.821 | 2.979 | 1.1387 | 1.2188 | 1.292 | 0.39955 | 0.40886 | 0.43677 | 0.13083
Fan Power [optional], W |  | 51 | 57 | 88 | 97 | 114 | 117 | 120 | 121 | 125 | 125.3 | 127 | 117 | 119 | 120 | 73 | 79 | 84 | 43
Efficiency, Cooling COP, kW/kW |  | 8.979 | 8.51 | 7.43 | 6.547 | 5.807 | 5.159 | 4.604 | 4.124 | 3.705 | 3.308 | 3.004 | 6.712 | 6.015 | 5.417 | 12.753 | 11.954 | 10.683 | 18.6782
Evaporator Water Pressure Drop, kPa |  | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29
Evaporator Entering Water Temperature, °C |  | 21.553 | 21.4713 | 21.2569 | 21.0477 | 20.8385 | 20.6261 | 20.4138 | 20.201 | 19.9887 | 19.7626 | 19.5667 | 18.9008 | 18.7415 | 18.572 | 17.6005 | 17.4944 | 17.3813 | 16.2472
Evaporator Water Flow Rate, L/s |  | 0.468 | 0.468 | 0.468 | 0.468 | 0.468 | 0.468 | 0.468 | 0.468 | 0.468 | 0.468 | 0.468 | 0.468 | 0.468 | 0.468 | 0.468 | 0.468 | 0.468 | 0.468
Refrigeration Capacity, kW | 15.6 | 13.068 | 12.9 | 12.49 | 12.08 | 11.675 | 11.251 | 10.828 | 10.404 | 9.98 | 9.528 | 9.137 | 7.803 | 7.485 | 7.146 | 5.202 | 4.99 | 4.764 | 2.495
Total Power, kW |  | 1.43 | 1.49 | 1.65 | 1.81 | 1.975 | 2.146 | 2.318 | 2.489 | 2.66 | 2.838 | 2.993 | 1.1328 | 1.2183 | 1.2941 | 0.39804 | 0.40602 | 0.43337 | 0.12739
Fan Power [optional], W |  | 51 | 57 | 88 | 97 | 114 | 117 | 120 | 121 | 125 | 125.3 | 127 | 117 | 119 | 120 | 73 | 79 | 84 | 43
Efficiency, Cooling COP, kW/kW |  | 9.138 | 8.658 | 7.57 | 6.674 | 5.911 | 5.243 | 4.671 | 4.18 | 3.752 | 3.357 | 3.053 | 6.888 | 6.144 | 5.522 | 13.069 | 12.29 | 10.993 | 19.5862
Evaporator Water Pressure Drop, kPa |  | 29.927 | 29.927 | 29.927 | 29.927 | 29.927 | 29.927 | 29.927 | 29.927 | 29.927 | 29.927 | 29.927 | 29.927 | 29.927 | 29.927 | 29.927 | 29.927 | 29.927 | 29.927
Evaporator Entering Water Temperature, °C |  | 22.1026 | 22.019 | 21.815 | 21.611 | 21.4094 | 21.1984 | 20.988 | 20.777 | 20.566 | 20.3411 | 20.1465 | 19.4827 | 19.3245 | 19.1558 | 18.1885 | 18.083 | 17.9705 | 16.8415
Evaporator Water Flow Rate, L/s |  | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48
IPLV.SI Calculation
Published Performance | Evaporator Leaving Water Temperature, °C7 | Condenser Entering Air Dry Bulb, °C and % Load
|  | 35.0, 100% |  | 27.0, 75% |  | 19.0, 50% |  | 13.0, 25%
Refrigeration Capacity, kW | 7 | 7.045 |  | 5.2838 |  | 3.5225 |  | 1.7612
Total Power, kW |  | 2.345 |  | 1.1709 |  | 0.46364 |  | 0.17331
Efficiency, Cooling COP (kW/kW) |  | 3.0043 |  | 4.5124 |  | 7.5975 |  | 10.1626
| IPLV.SI | 6.5636 | kW/kW
Published Performance | Evaporator Leaving Water Temperature, °C | Condenser Entering Air Dry Bulb, °C and % Load
|  | 35, 100% |  | 27, 75% |  | 19, 50% |  | 13, 25%
Capacity, kW | 13 | 9.014 |  | 6.7605 |  | 4.507 |  | 2.2535
Total Power, kW |  | 2.619 |  | 1.185 |  | 0.41631 |  | 0.13829
Efficiency, COP (W/W) |  | 3.442 |  | 5.705 |  | 10.826 |  | 16.296
| NPLV.SI | 9.2577 | kW/kW
Proper claims to AHRI Certification
Certified in accordance with the AHRI Air-Cooled Water-Chilling Packages Certification Program, which is based on AHRI Standard 550/590 (I-P) and AHRI Standard 551/591 (SI). Certified units may be found in the AHRI Directory at www.ahridirectory.org
AHRI Mark
Notes
1. The following apply to all ratings shown above: Evaporator Fouling Factor: 0.0180 m2·K/kW Condenser Fouling Factor: 0.000 m2·K/kW Atmospheric Pressure: 101.33 kPa 2. Highlighted fields represent the minimum required inputs. For units with continuous unloading, highlighted fields shall be provided. For units with discrete capacity steps, performance at each capacity step shall be provided. 3. All interpolated data within a units published performance is suject to AHRI testing. 4. All Published ratings for this unit shall be included in the values shown above. Performance at different conditions (i.e. different air and water temperatures, water flow rates, atmospheric pressures, fouling factors, etc.) shall not be published. 5. All values shall have the correct significant figures as in Table 8 of AHRI 551/591. 6. Full-Load Evaporator Water Temperature Change: 5.00°C. 7. Evaporator flow rates are to be held constant at full-load values for all part-load conditions.