## EWT49F
Chiltrix- Special Data For DHC
PROJECT NAME: | HBC - 49 degree EWT |  |  |  |  | CONTRACTOR:
LOCATION: | [5 empty] | SUBMITTED BY: |  | BRAD WASHBURN
ENGINEER: | [5 empty] | DATE: |  | 2019-05-13
| MODEL | 4HBXC3 | 4HBCX3 | 4HBCX3 | 4HBCX3 | 6HBCX3 | 6HBCX3 | 6HBCX3 | 6HBCX3 | 8HBCX3 | 8HBCX3 | 8HBCX3 | 8HBCX3 | 10HBCX3 | 10HBCX3 | 10HBCX3 | 10HBCX3 | 12HBCX3 | 12HBCX3 | 12HBCX3 | 12HBCX3
| QTY | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | *
BLOWER PERFORMANCE
TOTAL SUPPLY AIR | CFM | 400 | 400 | 400 | 400 | 600 | 600 | 600 | 600 | 800 | 800 | 800 | 800 | 1000 | 1000 | 1000 | 1000 | 1200 | 1200 | 1200 | 1200
ESP | IWC | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | *
FAN SPEED |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
MOTOR DATA
MOTOR RATING | HP | 0.14286 | 0.14286 | 0.14286 | 0.14286 | 0.14286 | 0.14286 | 0.14286 | 0.14286 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
POWER SUPPLY | V/PH/HZ | 120/1/60 | 120/1/60 | 120/1/60 | 120/1/60 | 120/1/60 | 120/1/60 | 120/1/60 | 120/1/60 | 120/1/60 | 120/1/60 | 120/1/60 | 120/1/60 | 120/1/60 | 120/1/60 | 120/1/60 | 120/1/60 | 120/1/60 | 120/1/60 | 120/1/60 | 120/1/60
AMP RATING | AMPS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
COOLING PERFORMANCE
ENTERING AIR TEMP. | DB °F | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80
ENTERING AIR TEMP. | WB °F | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67
LEAVING AIR TEMP. | DB °F | 58.8 | 59.5 | 60.2 | 61.4 | 58.9 | 59.4 | 60.3 | 61.5 | 60.2 | 60.7 | 61.5 | 62.4 | 60.3 | 60.8 | 61.4 | 62 | 61.5 | 62 | 62.5 | 63.3
LEAVING AIR TEMP. | WB °F | 58 | 58.5 | 59.1 | 60 | 57.9 | 58.4 | 59.1 | 60 | 58.9 | 59.4 | 60 | 60.7 | 59 | 59.4 | 59.9 | 60.4 | 59.9 | 60.3 | 60.7 | 61.1
TOTAL CAPACITY | MBH | 11.5 | 10.9 | 10.1 | 9.1 | 17.4 | 16.5 | 15.3 | 13.7 | 20.7 | 19.6 | 18.2 | 16.5 | 25.7 | 24.6 | 23.2 | 21.5 | 29.9 | 28.5 | 26.9 | 25
SENSIBLE CAPACITY | MBH | 9.3 | 9 | 8.7 | 8.2 | 14 | 13.6 | 13 | 12.3 | 17.5 | 17 | 16.4 | 15.5 | 21.8 | 21.2 | 20.6 | 19.8 | 26.5 | 25.8 | 25.1 | 23.9
LATENT CAPACITY | MBH | 2.2 | 1.9 | 1.4 | 0.9 | 3.4 | 2.9 | 2.3 | 1.4 | 3.2 | 2.6 | 1.8 | 1 | 3.9 | 3.4 | 2.6 | 1.7 | 3.4 | 2.7 | 1.8 | 1.1
ENTERING WATER TEMP. | °F | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49
LEAVING WATER TEMP | °F | 56.7 | 57.7 | 59.1 | 61.1 | 54.8 | 55.6 | 56.6 | 58.1 | 55.4 | 56.1 | 57.1 | 58.4 | 55.4 | 56 | 56.7 | 57.6 | 56.4 | 57.1 | 57.9 | 59
DELTA T | °F | 7.7 | 8.7 | 10.1 | 12.1 | 5.8 | 6.6 | 7.6 | 9.1 | 6.4 | 7.1 | 8.1 | 9.4 | 6.4 | 7 | 7.7 | 8.6 | 7.4 | 8.1 | 8.9 | 10
WATER FLOW RATE | GPM | 3 | 2.5 | 2 | 1.5 | 6 | 5 | 4 | 3 | 6.5 | 5.5 | 4.5 | 3.5 | 8 | 7 | 6 | 5 | 8 | 7 | 6 | 5
WATER PD | FT. WTR | 14.7 | 10.69 | 7.23 | 4.37 | 13.76 | 9.82 | 6.5 | 3.82 | 13.65 | 10.01 | 6.89 | 4.32 | 17.92 | 13.72 | 10.08 | 7 | 18.19 | 14.12 | 10.53 | 7.45
HEATING PERFORMANCE
ENTERING AIR TEMP. | DB °F | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ELECTRIC HEAT
CAPACITY | KW | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
POWER SUPPLY | V/PH/HZ | 120/1/60 | 120/1/60 | 120/1/60 | 120/1/60 | 120/1/60 | 120/1/60 | 120/1/60 | 120/1/60 | 120/1/60 | 120/1/60 | 120/1/60 | 120/1/60 | 120/1/60 | 120/1/60 | 120/1/60 | 120/1/60 | 120/1/60 | 120/1/60 | 120/1/60 | 120/1/60
RATED LOAD | AMPS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
LEAVING AIR TEMP. | DB °F | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HOT WATER
TOTAL SUPPLY AIR | CFM | 400 | 400 | 400 | 400 | 600 | 600 | 600 | 600 | 800 | 800 | 800 | 800 | 1000 | 1000 | 1000 | 1000 | 1200 | 1200 | 1200 | 1200
LEAVING AIR TEMP. | DB °F | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SENSIBLE CAPACITY | MBH | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ENTERING WATER TEMP. | °F | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
LEAVING WATER TEMP | °F | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DELTA T | °F | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
WATER FLOW RATE | GPM | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
WATER PD | FT. WTR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ELECTRICAL DATA
POWER SUPPLY | V/PH/HZ | 120/1/60 | 120/1/60 | 120/1/60 | 120/1/60 | 120/1/60 | 120/1/60 | 120/1/60 | 120/1/60 | 120/1/60 | 120/1/60 | 120/1/60 | 120/1/60 | 120/1/60 | 120/1/60 | 120/1/60 | 120/1/60 | 120/1/60 | 120/1/60 | 120/1/60 | 120/1/60
TOTAL | AMPS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
MIN. CIRCUIT AMPACITY | MCA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
MAX FUSE | MOCP
BELT DRIVE KIT # | MODEL

## EWT54F
Chiltrix- Special Data For DHC
PROJECT NAME: | HBC - 54 degree EWT |  |  |  |  | CONTRACTOR:
LOCATION: | [5 empty] | SUBMITTED BY: |  | BRAD WASHBURN
ENGINEER: | [5 empty] | DATE: |  | 2019-05-13
| MODEL | 4HBXC3 | 4HBCX3 | 4HBCX3 | 4HBCX3 | 6HBCX3 | 6HBCX3 | 6HBCX3 | 6HBCX3 | 8HBCX3 | 8HBCX3 | 8HBCX3 | 8HBCX3 | 10HBCX3 | 10HBCX3 | 10HBCX3 | 10HBCX3 | 12HBCX3 | 12HBCX3 | 12HBCX3 | 12HBCX3
| QTY | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | *
BLOWER PERFORMANCE
TOTAL SUPPLY AIR | CFM | 400 | 400 | 400 | 400 | 600 | 600 | 600 | 600 | 800 | 800 | 800 | 800 | 1000 | 1000 | 1000 | 1000 | 1200 | 1200 | 1200 | 1200
ESP | IWC | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | *
FAN SPEED |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
MOTOR DATA
MOTOR RATING | HP | 0.14286 | 0.14286 | 0.14286 | 0.14286 | 0.14286 | 0.14286 | 0.14286 | 0.14286 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
POWER SUPPLY | V/PH/HZ | 120/1/60 | 120/1/60 | 120/1/60 | 120/1/60 | 120/1/60 | 120/1/60 | 120/1/60 | 120/1/60 | 120/1/60 | 120/1/60 | 120/1/60 | 120/1/60 | 120/1/60 | 120/1/60 | 120/1/60 | 120/1/60 | 120/1/60 | 120/1/60 | 120/1/60 | 120/1/60
AMP RATING | AMPS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
COOLING PERFORMANCE
ENTERING AIR TEMP. | DB °F | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80
ENTERING AIR TEMP. | WB °F | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67
LEAVING AIR TEMP. | DB °F | 61.2 | 61.7 | 62.3 | 63.1 | 61.3 | 61.7 | 62.4 | 63.2 | 62.1 | 62.5 | 63.2 | 64.3 | 62.4 | 62.7 | 63.1 | 63.8 | 63.4 | 63.8 | 64.3 | 65.1
LEAVING AIR TEMP. | WB °F | 60.1 | 60.4 | 60.7 | 61.2 | 60.1 | 60.4 | 60.8 | 61.3 | 60.7 | 60.9 | 61.3 | 61.7 | 60.8 | 61 | 61.2 | 61.5 | 61.3 | 61.5 | 61.7 | 62.1
TOTAL CAPACITY | MBH | 9 | 8.6 | 8.2 | 7.5 | 13.4 | 12.9 | 12.2 | 11.3 | 16.5 | 15.9 | 15 | 13.9 | 20.3 | 19.7 | 19 | 18 | 24.2 | 23.5 | 22.6 | 21
SENSIBLE CAPACITY | MBH | 8.3 | 8.1 | 7.8 | 7.4 | 12.4 | 12.1 | 11.7 | 11.1 | 15.8 | 15.4 | 14.8 | 13.9 | 19.4 | 19.1 | 18.6 | 17.9 | 23.8 | 23.3 | 22.5 | 21
LATENT CAPACITY | MBH | 0.7 | 0.5 | 0.4 | 0.1 | 1 | 0.8 | 0.5 | 0.2 | 0.7 | 0.5 | 0.2 | 0 | 0.9 | 0.6 | 0.4 | 0.1 | 0.4 | 0.2 | 0.1 | 0
ENTERING WATER TEMP. | °F | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54
LEAVING WATER TEMP | °F | 60 | 60.9 | 62.1 | 64 | 58.5 | 59.1 | 60.1 | 61.5 | 59.1 | 59.8 | 60.7 | 61.9 | 59.1 | 59.6 | 60.3 | 61.2 | 60 | 60.7 | 61.5 | 62.4
DELTA T | °F | 6 | 6.9 | 8.1 | 10 | 4.5 | 5.1 | 6.1 | 7.5 | 5.1 | 5.8 | 6.7 | 7.9 | 5.1 | 5.6 | 6.3 | 7.2 | 6 | 6.7 | 7.5 | 8.4
WATER FLOW RATE | GPM | 3 | 2.5 | 2 | 1.5 | 6 | 5 | 4 | 3 | 6.5 | 5.5 | 4.5 | 3.5 | 8 | 7 | 6 | 5 | 8 | 7 | 6 | 5
WATER PD | FT. WTR | 14.7 | 10.69 | 7.23 | 4.37 | 13.76 | 9.82 | 6.5 | 3.82 | 13.65 | 10.01 | 6.89 | 4.32 | 17.92 | 13.72 | 10.08 | 7 | 18.19 | 14.12 | 10.53 | 7.45
HEATING PERFORMANCE
ENTERING AIR TEMP. | DB °F | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ELECTRIC HEAT
CAPACITY | KW | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
POWER SUPPLY | V/PH/HZ | 120/1/60 | 120/1/60 | 120/1/60 | 120/1/60 | 120/1/60 | 120/1/60 | 120/1/60 | 120/1/60 | 120/1/60 | 120/1/60 | 120/1/60 | 120/1/60 | 120/1/60 | 120/1/60 | 120/1/60 | 120/1/60 | 120/1/60 | 120/1/60 | 120/1/60 | 120/1/60
RATED LOAD | AMPS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
LEAVING AIR TEMP. | DB °F | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HOT WATER
TOTAL SUPPLY AIR | CFM | 400 | 400 | 400 | 400 | 600 | 600 | 600 | 600 | 800 | 800 | 800 | 800 | 1000 | 1000 | 1000 | 1000 | 1200 | 1200 | 1200 | 1200
LEAVING AIR TEMP. | DB °F | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SENSIBLE CAPACITY | MBH | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ENTERING WATER TEMP. | °F | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
LEAVING WATER TEMP | °F | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DELTA T | °F | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
WATER FLOW RATE | GPM | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
WATER PD | FT. WTR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ELECTRICAL DATA
POWER SUPPLY | V/PH/HZ | 120/1/60 | 120/1/60 | 120/1/60 | 120/1/60 | 120/1/60 | 120/1/60 | 120/1/60 | 120/1/60 | 120/1/60 | 120/1/60 | 120/1/60 | 120/1/60 | 120/1/60 | 120/1/60 | 120/1/60 | 120/1/60 | 120/1/60 | 120/1/60 | 120/1/60 | 120/1/60
TOTAL | AMPS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
MIN. CIRCUIT AMPACITY | MCA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
MAX FUSE | MOCP
BELT DRIVE KIT # | MODEL

## Sheet2
Chiltrix- Special Data For DHC
PROJECT NAME: | HBC - 59 degree EWT |  |  |  |  | CONTRACTOR:
LOCATION: | [5 empty] | SUBMITTED BY: |  | BRAD WASHBURN
ENGINEER: | [5 empty] | DATE: |  | 2019-05-13
| MODEL | 4HBXC3 | 4HBCX3 | 4HBCX3 | 4HBCX3 | 6HBCX3 | 6HBCX3 | 6HBCX3 | 6HBCX3 | 8HBCX3 | 8HBCX3 | 8HBCX3 | 8HBCX3 | 10HBCX3 | 10HBCX3 | 10HBCX3 | 10HBCX3 | 12HBCX3 | 12HBCX3 | 12HBCX3 | 12HBCX3
| QTY | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | *
BLOWER PERFORMANCE
TOTAL SUPPLY AIR | CFM | 400 | 400 | 400 | 400 | 600 | 600 | 600 | 600 | 800 | 800 | 800 | 800 | 1000 | 1000 | 1000 | 1000 | 1200 | 1200 | 1200 | 1200
ESP | IWC | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | *
FAN SPEED |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
MOTOR DATA
MOTOR RATING | HP | 0.14286 | 0.14286 | 0.14286 | 0.14286 | 0.14286 | 0.14286 | 0.14286 | 0.14286 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
POWER SUPPLY | V/PH/HZ | 120/1/60 | 120/1/60 | 120/1/60 | 120/1/60 | 120/1/60 | 120/1/60 | 120/1/60 | 120/1/60 | 120/1/60 | 120/1/60 | 120/1/60 | 120/1/60 | 120/1/60 | 120/1/60 | 120/1/60 | 120/1/60 | 120/1/60 | 120/1/60 | 120/1/60 | 120/1/60
AMP RATING | AMPS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
COOLING PERFORMANCE
ENTERING AIR TEMP. | DB °F | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80
ENTERING AIR TEMP. | WB °F | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67
LEAVING AIR TEMP. | DB °F | 64 | 64.4 | 65 | 66.1 | 64.1 | 64.5 | 65 | 66.1 | 65 | 65.4 | 66.1 | 67.1 | 65.2 | 65.5 | 65.9 | 66.6 | 66.3 | 66.6 | 67.1 | 67.8
LEAVING AIR TEMP. | WB °F | 61.7 | 61.9 | 62.1 | 62.4 | 61.6 | 61.8 | 62 | 62.3 | 62 | 62.2 | 62.4 | 62.7 | 62 | 62.1 | 62.3 | 62.5 | 62.4 | 62.5 | 62.7 | 62.9
TOTAL CAPACITY | MBH | 7 | 6.8 | 6.5 | 6 | 10.6 | 10.3 | 9.9 | 9.2 | 13 | 12.7 | 12.1 | 11.2 | 16.4 | 16 | 15.5 | 14.7 | 19.7 | 19.2 | 18.5 | 17.5
SENSIBLE CAPACITY | MBH | 7 | 6.8 | 6.5 | 6 | 10.6 | 10.3 | 9.9 | 9.2 | 13 | 12.7 | 12.1 | 11.2 | 16.4 | 16 | 15.5 | 14.7 | 19.7 | 19.2 | 18.5 | 17.5
LATENT CAPACITY | MBH | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ENTERING WATER TEMP. | °F | 59 | 59 | 59 | 59 | 59 | 59 | 59 | 59 | 59 | 59 | 59 | 59 | 59 | 59 | 59 | 59 | 59 | 59 | 59 | 59
LEAVING WATER TEMP | °F | 63.6 | 64.4 | 65.5 | 67 | 62.5 | 63.1 | 63.9 | 65.1 | 63 | 63.6 | 64.4 | 65.4 | 63.1 | 63.6 | 64.2 | 64.9 | 63.9 | 64.5 | 65.2 | 66
DELTA T | °F | 4.6 | 5.4 | 6.5 | 8 | 3.5 | 4.1 | 4.9 | 6.1 | 4 | 4.6 | 5.4 | 6.4 | 4.1 | 4.6 | 5.2 | 5.9 | 4.9 | 5.5 | 6.2 | 7
WATER FLOW RATE | GPM | 3 | 2.5 | 2 | 1.5 | 6 | 5 | 4 | 3 | 6.5 | 5.5 | 4.5 | 3.5 | 8 | 7 | 6 | 5 | 8 | 7 | 6 | 5
WATER PD | FT. WTR | 14.7 | 10.69 | 7.23 | 4.37 | 13.76 | 9.82 | 6.5 | 3.82 | 13.65 | 10.01 | 6.89 | 4.32 | 17.92 | 13.72 | 10.08 | 7 | 18.19 | 14.12 | 10.53 | 7.45
HEATING PERFORMANCE
ENTERING AIR TEMP. | DB °F | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ELECTRIC HEAT
CAPACITY | KW | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
POWER SUPPLY | V/PH/HZ | 120/1/60 | 120/1/60 | 120/1/60 | 120/1/60 | 120/1/60 | 120/1/60 | 120/1/60 | 120/1/60 | 120/1/60 | 120/1/60 | 120/1/60 | 120/1/60 | 120/1/60 | 120/1/60 | 120/1/60 | 120/1/60 | 120/1/60 | 120/1/60 | 120/1/60 | 120/1/60
RATED LOAD | AMPS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
LEAVING AIR TEMP. | DB °F | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HOT WATER
TOTAL SUPPLY AIR | CFM | 400 | 400 | 400 | 400 | 600 | 600 | 600 | 600 | 800 | 800 | 800 | 800 | 1000 | 1000 | 1000 | 1000 | 1200 | 1200 | 1200 | 1200
LEAVING AIR TEMP. | DB °F | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SENSIBLE CAPACITY | MBH | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ENTERING WATER TEMP. | °F | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
LEAVING WATER TEMP | °F | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DELTA T | °F | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
WATER FLOW RATE | GPM | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
WATER PD | FT. WTR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ELECTRICAL DATA
POWER SUPPLY | V/PH/HZ | 120/1/60 | 120/1/60 | 120/1/60 | 120/1/60 | 120/1/60 | 120/1/60 | 120/1/60 | 120/1/60 | 120/1/60 | 120/1/60 | 120/1/60 | 120/1/60 | 120/1/60 | 120/1/60 | 120/1/60 | 120/1/60 | 120/1/60 | 120/1/60 | 120/1/60 | 120/1/60
TOTAL | AMPS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
MIN. CIRCUIT AMPACITY | MCA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
MAX FUSE | MOCP
BELT DRIVE KIT # | MODEL
F